POWER CABLE ACCESSORIES                                  FLYPOWER

BH-EC

| 250A screened elbow connector Features/Applications： BH-EC 250A screened elbow connector, made of EPDM rubber, is used for indoor Applications. The main body is composed of inner conductive layer, insulating layer and outer conductive layer, suitable for the connection of XLPE cables up to 12/20kV to transformers, switchgear, motors and other equipment with a separable connector. 100% factory tested before shipment, quality guaranteed; Suitable adaptors（stress cone）easy and simple installation; The stress cone covers the cable range of 35mm2 -125mm2; Compact design to suit various installations; Combined with insulation, sealing and touchable screened; Meet: IEC60502-4, GB12706.4. Specification Size(mm); Main insulation diameter (mm); Cable cross-seciton. 8.7/15 kV(mm2); 12/20kV(mm2). Φ 15; 18-20; 35-50; 35. Φ 18; 20-23; 70-95; 50-70. Φ 21; 23-26; 120-150; 95-120. |  |
| --- | --- |
| Technical Data Performance; HCE-102; HCE-202. Rated voltage; 8.7/15（17.5）kV; 12/20（24）kV. Max. system voltage; 17.5kV; 24kV. Continuous current; 250A; 250A. Partial discharge; 15kV/≤10pC; 20kV/≤10pC. A.C withstand voltage; 39kV/5min; 54kV/5min. Thermal short circuit; 22.8kA/2s; 24kA/2s. Dynamic short circuit; 80.8kA/10ms; 84.8kA/10ms. Design and structure (mm) Pin contact Insulating layer Inner screen Outer screen Compression lug Earthing eye Pulling eye Testing point Main Compounds Elbow Connector body Pin Compression lugs Mechanical metal pad Special pin Spanner |  |

Conductive rod